Permit #:

Date:

Location:

Inspector:

HVAC/In-Floor Heating Inspection Checklist

- Township stamped plans and heat designs are onsite.

- Clearance between plenum and combustible materials is acceptable.

- Supply ducts and fittings are non-combustible.

- Supply trunk is not nailed/fastened directly to floor joists.

- ‘S’ and drive cleats are installed for rectangular ducting.

- Supply and return ducts in unheated spaces are insulated with R-12 min.

- Supply ducts are sealed with tape or mastic (class C)

- Vertical clearance to all ducts in basement minimum 6’5” (1.95m)

- A return air is installed on each story.

- Return air chases are backed, fire stopped at ends, have no obstructions.

- Return air inlets are not located in garage, kitchen, furnace, laundry rm.

- Exhaust fan ducts in attic are wrapped with insulation/vapour barrier.

- Horizontal flexible exhaust ducts do not exceed 13 ft. (4m) in length.

- Kitchen exhaust ducts are cleanable, or cleanable filter is installed.

- Butterfly dampers are installed at each heat register outlet.

- Furnace, HRV, Boiler, Water heater meets energy efficiencies. (houses)

- Exhaust air intake (HRV) or fans are installed in kitchens and in bathrooms without windows.

In-Floor Heating

- Under-slab insulation is complete, taped and sealed at perimeter. (R10)

- Heating pipe is complete, spaced and installed as per radiant design.

- Heating pipe is charged with air to minimum 60 psi or 2 times the system operating pressure.